# Q2 审题及PPT内容对应
Question interpretation and PPT mapping

## 1 审题 / Interpreting the task

题目要求列出工业电缆选型及截面的影响因素，并解释原因；无需逐项抄表或计算一个最终截面。

List factors affecting industrial cable selection and sizing and explain their effects qualitatively. Reproducing every table or calculating a final cable size is unnecessary.

## 2 本版内容边界 / Scope of this revision

正文以《Electrical Distribution System II》S78–S83的Cable及Cable Sizing内容为限。题目指定的三份图表用于识别安装方式、查载流量、压降及修正系数，不把图表的每项细节扩展成新的答题主题。

The answer follows Cable and Cable Sizing in Electrical Distribution System II, S78–S83. The three supplied extracts support identification of installation methods, current and voltage-drop ratings, and correction factors; every table detail is not made into an additional answer topic.

## 3 先区分选型和截面 / Selection versus sizing

S78说明结构选型；S79列载流量、压降、损耗三项截面标准；S80列外部影响、安装、负载、压降及能源效益。正文框架直接来自这些项目。

S78 covers construction; S79 gives capacity, voltage drop and power loss as sizing criteria; S80 lists external influences, installation, loading, voltage drop and efficiency. These establish the answer framework.

## 正式答案第1–5项对应 / Mapping factors 1–5

| 要点 / Point | 判读及含义 / Interpretation |
| --- | --- |
| 1 结构及材料 Construction | S78、S80：铜／铝、芯数、PVC／XLPE、护套及铠装；解释为什么必须使用匹配电缆类型的额定资料。 S78/S80: material, cores, insulation, sheath and armour; use rating data matching the selected type. |
| 2 外部影响 External influences | S80：评估环境条件及一般特性，以指定适当设备。正文保持该层次，不另列课件未展开的专门要求。 S80: assess environmental conditions and general characteristics for suitable selection; retain that level of detail. |
| 3 安装方式 Installation | S80–S81：先选电缆类型及安装方式，再查载流量；Appendix 7辅助确定参考Method。 S80–S81: select type and installation before rating; Appendix 7 identifies the reference Method. |
| 4 负载 Loading | S80–S81：Loading及Ib决定电流需求。解释电流增加与导体温升、截面之间的关系。 S80–S81: loading and Ib establish demand; explain the relation to heating and size. |
| 5 温度 Temperature | S81：Ca；S83示例以45°C及Ca＝0.79说明修正后的选线要求。 S81: Ca; S83 illustrates it with 45°C and Ca = 0.79. |

# 4 其余因素及三组图表的作用
Remaining factors and the three table groups

| 要点 / Point | 判读及含义 / Interpretation |
| --- | --- |
| 6 成组 / Grouping | S81明确指出围护或成束回路的Cg可使截面显著增加，并给出It ≥ In/Cg。答案解释其原因是互相加热。 S81 states that Cg for enclosed/bunched circuits may significantly increase size and gives It ≥ In/Cg; the explanation is mutual heating. |
| 7 隔热 / Insulation | S81列Ci。答案只解释隔热阻碍散热及影响额定值，不扩展成完整隔热设计计算。 S81 lists Ci; explain restricted cooling and the rating effect without adding a full insulation-design exercise. |
| 8 保护器件 Protective device | S81列In及Cd，半封闭熔断器Cd＝0.725，并给出It的修正关系。 S81 lists In and Cd, gives Cd = 0.725 for semi-enclosed fuses, and relates them to required It. |
| 9 长度及压降 Length and voltage drop | S81列长度；S82给压降资料及公式；S83把上游压降纳入示例。 S81 lists length; S82 supplies voltage-drop inputs and equation; S83 allows for upstream drop. |
| 10 损耗及能源效益 Loss and efficiency | S79列Power loss，S80列Energy efficiency。电阻及截面之间的解释用于说明该因素为何影响选线。 S79 lists power loss and S80 energy efficiency; relate resistance and cross-section to the selection consequence. |

## 三组表各解决什么问题 / What each table group determines

| 要点 / Point | 判读及含义 / Interpretation |
| --- | --- |
| Appendix 7 | 确定实际安装条件对应的参考Method，再选A6(1)栏位。不同安装方式的散热不同。 Identify the reference Method for the actual installation, then select the A6(1) column; installation changes cooling. |
| Table A6(1) | 按电缆类型、截面、参考Method及相制选载流量；压降页另按相制及排列选值。表头为单芯、PVC绝缘、非铠装铜电缆，参考环境30°C、导体70°C。 Select current ratings by type, size, Method and phase; use the corresponding voltage-drop data. The main table covers single-core, PVC-insulated, non-armoured copper cable at 30°C ambient/70°C conductor temperature. |
| Correction tables | 为S81中的Ca、Cg、Ci、Cd提供适用资料。A5(1)／A5(2)区分温度修正的保护条件；A5(3)、A5(4)、A5(5)分别对应成组、隔热及器件类型。各表只在适用时采用。 Provide applicable Ca, Cg, Ci and Cd data. A5(1)/A5(2) distinguish protection conditions for temperature correction; A5(3), A5(4) and A5(5) cover grouping, insulation and device type. Apply each only where relevant. |

# 5 PPT载流量关系及示例判读
PPT current-rating relation and example

## S81：修正关系 / Correction relation

It ≥ In / (Ca × Cg × Ci × Cd)

It为所需表列载流量；In为保护器件额定电流；Ca、Cg、Ci、Cd分别为环境温度、成组、隔热及器件修正。系数小于1时，所需表列载流量增大，查表可能需要更大的截面。先按实际安装选择基准及适用系数，不重复计入同一安装影响。

It is the required tabulated current rating; In is the protective-device rating. Ca, Cg, Ci and Cd represent ambient, grouping, insulation and device corrections. Factors below unity increase required It and may lead to a larger size. Match the base rating and applicable factors to the installation without duplicating an effect.

## S83：示例仅用于理解查表 / Example for understanding table use

PPT给定三相、20A MCB、45°C、表面管道、40m线路；示例以20A负载和380V计算，上游压降1%。这些是课件例题条件，不能当作Q2已给定的参数。

The PPT example specifies three phases, a 20A MCB, 45°C, surface conduit and a 40m route. Its calculation uses 20A load, 380V and 1% upstream drop. These are example conditions, not parameters supplied by Q2.

| 要点 / Point | 判读及含义 / Interpretation |
| --- | --- |
| ① 温度修正 Temperature | A5(1)中Ca＝0.79，故It ≥ 20/0.79＝25.3A。 Ca = 0.79 from A5(1); required It ≥ 25.3A. |
| ② 查载流量 Current rating | 表面管道对应Method 3；A6(1)中4mm²三相值28A，满足25.3A需求。 Surface conduit uses Method 3; the 4mm² three-phase rating is 28A, meeting 25.3A. |
| ③ 查压降 Voltage drop | 同一电缆三相压降数据9.5mV/A/m：9.5×20×40/1000＝7.6V，约为380V的2%。 At 9.5mV/A/m, drop is 7.6V, about 2% of 380V. |
| ④ 合并上游 Include upstream | PPT采用总压降4%；上游1%后余3%，本段约2%，符合例题条件。说明通过载流量后仍需查压降。 Under the example’s 4% total allowance, 1% upstream leaves 3%; approximately 2% meets that condition. Capacity and voltage drop are separate checks. |

正式答案不需要写这组计算：题目要求的是影响因素及定性解释，例题只是说明为什么温度、安装方式、长度及负载都必须考虑。

The written answer does not need these calculations. They explain why temperature, installation, length and loading matter to the qualitative task.

# 6 压降、损耗与最终答题范围
Voltage drop, loss and final answer scope

## S82：长度为什么影响选线 / Why length affects selection

ΔV = v × Ib × L / 1000

v为表列压降数据（mV/A/m），Ib为设计电流（A），L为线路长度（m）。在表格适用条件下，电流或长度增大会增加压降。S82要求知道电缆类型、截面、安装方式、长度、交流／直流及负载，因此正文第9项覆盖这些变量。

v is the tabulated voltage-drop value in mV/A/m, Ib the design current in A, and L the route length in m. Under the table’s conditions, greater current or length increases drop. S82 requires type, size, installation, length, a.c./d.c. circuit and load; factor 9 covers these inputs.

S82采用电源调压6%、设备容许10%，得出配电系统4%；另列实践分配为上升干线1.5%、馈线／最终回路2.5%。S83按已知上游1%分配余下3%。这些是课件中的条件和分配，定性答案无需逐个抄出，也不把它们表述为所有工程的统一数值。

S82 derives 4% for distribution from 6% source regulation and 10% equipment allowance, and lists a practical split of 1.5% rising mains and 2.5% feeder/final circuit. S83 allocates 3% after its specified 1% upstream drop. These are course conditions and allocations, not universal design values, and need not be reproduced in a qualitative answer.

## S79–S80：为何保留损耗 / Why retain losses

PPT将功率损耗列为截面标准，将能源效益列为选线因素。因此第10项必须保留。其定性含义是：同一电流下，降低电阻可降低损耗，增大截面是影响电阻的方式之一；不用增加经济计算或课件之外的设计要求。

The PPT names power loss as a sizing criterion and energy efficiency as a selection factor, so factor 10 is retained. Qualitatively, lower resistance reduces loss at the same current, and cross-section affects resistance. No additional economic calculation or design requirement is needed.

## 正式答案的组织方式 / Organisation of the written answer

前3项解释“选择什么电缆、在什么条件下安装”；第4–8项解释“负载及热条件如何决定所需载流量”；第9–10项补齐“压降和损耗”两项标准。每项都包含因素、影响及选型结果。这样覆盖PPT的全部选线框架，同时保持题目要求的定性层次。

Factors 1–3 address cable choice and installation; 4–8 explain how demand and thermal conditions determine current-rating needs; 9–10 complete the voltage-drop and power-loss criteria. Each links a factor to its effect and selection consequence, covering the PPT framework at the requested qualitative level.

另一份Word仅保留可抄写的中英答案，不含本稿的页码对应、审题提示及例题计算。

The companion Word contains only the bilingual written answer, without slide mapping, interpretation notes or worked calculations.